{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["暖通空调"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"暖通空调","index":0,"n_rows":59,"n_cols":11,"rows_kept":59,"merged":[[0,0,0,10],[13,0,13,10],[41,0,41,10]],"flags":["formulas_cached_only"]}
["暖通空调-询价单"]
["序号","名称","规格、型号","单位","品牌、厂家","等级","含税到场价","税点（%）","不含税到场价","电话号码","备注"]
[1,"组合全新风净化空调机组（变频风机）","1.送风量:5000CMH\n2.新风量:5000CMH\n3.制热量:76KW、制冷量：72kw\n4.电加热:10KW\n5.加湿量:32Kg/h\n6.含G4、F8过滤器\n7.直接蒸发式，变频压缩机","台"]
[2,"环保冷媒充注","符合国家规范的环保冷媒。与AHU空调机组配套","Kg"]
[3,"玻璃钢离心风机","1.型号:6C 5.5KW\n2.风量：7367-14734m?/h，\n3.机外余压：881-1389PA\n4.变频风机\n5.左旋90度\n6.风机进出口：500*400mm","台"]
[4,"防爆型轴流风机","1.型号:SLF-01\n2.风量：1182m3/h，\n3.全压：75PA\n4.转速：1450r/min\n5.电机功率：0.37Kw","台"]
[5,"排气扇","1.型号:300H-6\n2.风量：450m?/h，\n3.机外余压：50PA","台"]
[6,"高效过滤箱","1.处理风量：5000m?/h\n2.效率 ：H14 99.995%@0.3um\n3.额定风量 : 2.5m/s@5000m3/h\n4.初阻力 :2.5m/s@250Pa","台"]
[7,"玻璃钢风机防雨帽","1.配套玻璃钢排风机","个"]
[8,"风机软对接","1.配套玻璃钢排风机，空调机组\n周长2m以内","套"]
[9,"风机弹簧减震器",null,"个"]
[10,"空调减震器",null,"个"]
[11,"不锈钢保温凝结水箱","400×400×300，每个箱体配DN25高温软管2米","套"]
["净化空调风系统"]
[1,"手动对开多叶调节阀","1、规格：500*400               2、材质：净化专用，内外镀锌，内衬洁净密封胶圈。钢板厚度：阀本体1.2mm，法兰2.0mm","个"]
[2,"手动对开多叶调节阀","1、规格：320x200                 2、材质：净化专用，内外镀锌，内衬洁净密封胶圈。钢板厚度：阀本体1.2mm，法兰2.0mm","个"]
[3,"手动对开多叶调节阀","1、规格：200x200                 2、材质：净化专用，内外镀锌，内衬洁净密封胶圈。钢板厚度：阀本体1.2mm，法兰2.0mm","个"]
[4,"电动对开多叶调节阀","1、规格：400*320              \n2、材质：净化专用，内外镀锌，内衬洁净密封胶圈。钢板厚度：阀本体1.2mm，法兰2.0mm","个"]
[5,"电动对开多叶调节阀","1、规格：320x200                 2、材质：净化专用，内外镀锌，内衬洁净密封胶圈。钢板厚度：阀本体1.2mm，法兰2.0mm","个"]
[6,"电动对开多叶调节阀","1、规格：250x200                 2、材质：净化专用，内外镀锌，内衬洁净密封胶圈。钢板厚度：阀本体1.2mm，法兰2.0mm","个"]
[7,"电动对开多叶调节阀","1、规格：200x200                 2、材质：净化专用，内外镀锌，内衬洁净密封胶圈。钢板厚度：阀本体1.2mm，法兰2.0mm","个"]
[8,"电动对开多叶调节阀","1、规格：φ250                      2、材质：镀锌板","个"]
[9,"电动密闭阀","1、规格：500*400                       2、材质：1.2mm厚镀锌材质制作                                      3、带开关型信号执行器","个"]
[10,"70℃电动不锈钢防火阀\n（常开)","1、规格：500*400                  2、材质：304#不锈钢板制作,法兰2.0mm，防腐喷涂。                    3、3C认证","个"]
[11,"微孔板消声器","1、规格：500x400x1200                 2、材质：净化专用，内外镀锌，内衬50mm消声棉。钢板厚度：本体1.2mm，法兰2.0mm","个"]
[12,"新风防雨百叶  ","1、规格：喉部尺寸1800*300         2、材质：1.2mm铝合金，带阻尼滤网","个"]
[13,"高效过滤器","1、规格型号：GKF-5，L=500CMH                              2、说明：高效过滤效率≥99.95%@≥0.5μm。","个"]
[14,"高效过滤器","1、规格型号：GKF-10，L=1000CMH                             2、说明：高效过滤效率≥99.999%@≥0.5μm。","个"]
[15,"余压阀","1、规格：400x250                     2、材质：净化专用，内外镀锌，内衬洁净密封胶圈。钢板厚度：阀本体1.2mm，法兰2.0mm","个"]
[16,"门绞式铝合金                      百叶风口","1、规格：600*500                   2、材质：1.2mm铝合金，带阻尼滤网","个"]
[17,"门绞式铝合金                      百叶风口","1、规格：500*400                 2、材质：1.2mm铝合金，带阻尼滤网","个"]
[18,"门绞式铝合金                      百叶风口","1、规格：400*300                  2、材质：1.2mm铝合金，带阻尼滤网","个"]
[19,"格栅百叶风口","1、规格：300*300                2、材质：1.2mm铝合金，带阻尼滤网","个"]
[20,"净化型风管","1、使用位置：用于长边b≤320风管                        \n2、材质：镀锌风管，风管厚度 \nδ=0.6mm                               3、接口形式：法兰                                ","m2"]
[21,"净化型风管","1、使用位置：用于长边400≤b≤630风管                           \n2、材质：镀锌风管，风管厚度 \nδ=0.75mm                               3、接口形式：法兰                                ","m2"]
[23,"冷媒铜管","1.输送介质:冷媒水、气\n2.材质:铜管,穿20mm厚保温套管\n3.型号、规格:φ12.7*1.0\n4.连接方式:螺纹连接\n","m"]
[24,"冷媒铜管","1.输送介质:冷媒水、气\n2.材质:铜管,穿20mm厚保温套管\n3.型号、规格:φ28*1.2\n4.连接方式:螺纹连接\n","m"]
[25,"冷凝水管","1.输送介质:冷凝水\n2.材质: PPR材质，穿15mm厚B1级橡塑保温套管\n3.型号、规格: DN20\n4.连接方式: 法兰连接\n","m"]
[26,"PPR加湿水管","1.输送介质:加湿水\n2.材质: PPR管\n3.型号、规格:DN20\n4.连接方式: 法兰连接","m"]
[27,"球阀","1、型号：DN20                              2、材质：PPR材质                        3、连接方式：法兰连接","个"]
[28,"压力表","1、型号：±60Pa","个"]
["净化空调系统动力布线与智能化控制"]
[1,"洁净空调机组动力配电柜","净化空调机组动力控制柜，功率72KW，控制AHU-1净化空调机组及PF-01排风机组","套"]
[2,"洁净系统智能控制系统 ","洁净系统智能控制系统（柜）。含编程软件、通讯装置（通讯模块、通讯协议、通讯接口）、CPU及扩展模块","套"]
[3,"变频器","1.规格：5.5kw","套"]
[4,"变频器","1.规格：4.0kw","套"]
[5,"空调机组液晶触摸控制面板","全彩触摸屏","套"]
[6,"风阀角度传感器","1.角度记忆","个"]
[7,"新风温湿度传感器","1、型号：QFM4160                          2、HR: 0～100％RH                        3、T: -40~80℃","台"]
[8,"房间温湿度传感器","1、型号：QFM4160                          2、HR: 0～100％RH                        3、T: -40~80℃","台"]
[9,"模拟量风阀执行器","1.名称:模拟量风阀执行器\n2.规格:10N(响应时间2S)\n3.技术参数：\n供电：24VDAC；\n信号：0~10V\n4.功能：\n房间排风量控制；\n"]
[10,"房间压差传感器","1、型号：761-11                           2、量程：±50Pa\n3、精度：全量程 ±0.5 %。\n4、输入：pt100，四线制。\n5、输出：4～20mA或0～10V。                           6、材质：高精度硅压阻式差压芯体                                        7、稳定性:0.15%FS/y ","台"]
[11,"管道静压传感器","1、量程：0-1000Pa\n2、精度：全量程 ±0.5 %。\n3、输入：pt100，四线制。\n4、输出：4～20mA或0～10V。                           5、材质：高精度硅压阻式差压芯体                                         6、稳定性:0.15%FS/y ","台"]
[12,"送风风速传感器","1.名称:风速传感器\n2.规格:可选电压型或电流型\n3.技术参数：测量范围：0-5m/s或0-10m/s切换；\n供电：DC24V","只"]
[13,"排风高效过滤器失效检测报警装置","可标定(50-500)Pa,24VAC/DC","套"]
[14,"高效失效检测报警装置","可标定(50-500)Pa,24VAC/DC","套"]
[15,"中效失效检测报警装置","可标定(50-500)Pa,24VAC/DC","套"]
[16,"机组缺风保护报警装置","可标定(50-500)Pa,25VAC/DC","套"]
[17,"机组高温保护报警装置","1、量程：0℃-250℃","套"]